## P&G
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200 A
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 1: PRELIMINARY AND GENERAL
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
1 | 1200 A | SECTION 1: PRELIMINARY AND GENERAL
1.1 | 8.3 | FIXED-CHARGE ITEMS
1.1.1 | 8.3.1 | Contractual Requirements | Sum | 1
1.1.2 | PSA 8.12 | Contractor's initial obligations in respect of the Occupational Health and Safety Act and Construction Regulations | Sum | 1
1.1.3 | PSA 8.12 | Submission of the Health and Safety File | Sum | 1
1.1.4 | PSA 8.13 | Submission of the Environmental Management Plan | Sum | 1
| 8.3.2 | Establish Facilities on the Site :
a) Facilities for Engineer (SABS 1200 AB)
1.1.5 |  | Furnished Office | Sum | 1
1.1.6 |  | Nameboards | No | 2
| PSA 8.4.2.2 | b) Facilities for Contractor
1.1.7 |  | Offices and storage sheds | Sum | 1
1.1.8 |  | Ablution and latrine facilities | Sum | 1
1.1.9 |  | Tools and equipment | Sum | 1
1.1.10 |  | Water supplies, electric power and communications | Sum | 1
1.1.11 |  | Dealing with water (Subclause 5.5) | Sum | 1
1.1.12 |  | Access (Subclause 5.8) | Sum | 1
1.1.13 |  | Plant | Sum | 1
1.1.14 | 8.3.3 | Other fixed-charge obligations | Sum | 1
1.1.15 | 8.3.4 | Remove Engineer's and Contractor's Site establishment on completion | Sum | 1
1.2 | 8.4 | TIME-RELATED ITEMS
1.2.1 | 8.4.1 | Contractual Requirements | Sum | 1
1.2.2 | PSA 8.12 | Contractor's initial obligations in respect of the Occupational Health and Safety Act and Construction Regulations | Sum | 1
| 8.4.2 | Operate and maintain facilities on the Site:
| 8.4.2.1 | a) Facilities for Engineer for duration of construction (SABS 1200 AB)
1.2.3 | PSAB 3.2 | Furnished Office | Sum | 1
1.2.4 | PSAB 3.1 | Nameboards | No | 1
1.2.5 | PSA 8.14 | Remuneration of the Community Liaison Officer | Month | 15
1.2.6 | PSA 8.15 | Handling fee in respect of Remuneration of the Community Liaison Officer | %
1.2.9 | PSA 8.13 | Compliance with the specified environmental requirements | Sum | 1
| 8.4.2.2 | b) Facilities for Contractor for duration of construction, except where otherwise stated
1.2.10 |  | Offices and storage sheds | Sum | 1
1.2.11 |  | Ablution and latrine facilities | Sum | 1
1.2.12 |  | Tools and equipment | Sum | 1
CARRIED FORWARD
BROUGHT FORWARD
1.2.13 |  | Water supplies, electric power and communications | Sum | 1
1.2.14 |  | Dealing with water (Subclause 5.5) | Sum | 1
1.2.15 |  | Access (Subclause 5.8) | Sum | 1
1.2.16 |  | Plant | Sum | 1
1.2.17 | 8.4.3 | Supervision | Sum | 1
1.2.18 | 8.4.4 | Company and head office overhead costs | Sum | 1
1.2.19 | 8.4.5 | Other time-related obligations personnel | Sum | 1
1.2.20 | 8.4.5 | Provision of Security Personnel | Month | 15
1.2.21 | PSA 8.12 | Provision of full-time construction safety officer | Sum | 1
PSA 8.5
1.2.26 |  | a)Acceptance testing of material and workmanship called for by the Engineer at a nominated laboratory | Prov Sum | 1 | 20000 | 20000
1.2.27 |  | b) Overheads, charges and profit on item 1.2.26 | % | 20000
1.2.28 |  | c) Permanent Signage on Site | Sum | 1
1.2.29 |  | d) Overheads, charges and profit on item 1.2.28 | %
1.2.30 |  | e) Allowance for the Quality Control inspections at Original Equipment Manufacturer | Prov Sum | 1 | 50000 | 50000
1.2.31 |  | f) Overheads, charges and profit on item 1.2.30 | % | 50000
PAYMENTS TO SERVICE AUTHORITIES
1.2.32 |  | Supervision charges and assistance and relocating services (powerline) by Service Authorities | PSum | 1 | 30000 | 30000
1.2.33 |  | Overheads, charges and profit on Item No 1.3.4 | % | 30000
1.2.34 | 8.8.3 | TEMPORARY WORKS | Sum | 1
TRAINING
1.2.35 | D1.4.1 | Allowance for accredited training of local unskilled labour | Prov Sum | 1 | 150000 | 150000
1.2.36 |  | Charges on profit on item 1.3.2 above | % | 150000
TOTAL CARRIED FORWARD TO SUMMARY

## Dayworks
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | PSA 8.7
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 2: DAYWORKS
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
2 | PSA 8.7 | SECTION 2: DAYWORKS
2.1 | PSA 8.7, SABS 1200 A and AB | Labour
2.1.1 |  | Foreman | hr | 80
2.1.2 |  | Steel Fixer | hr | 20
2.1.3 |  | Concretor | hr | 20
2.1.4 |  | Chargehand | hr | 40
2.1.5 |  | Artisan (Welder, Plumber, etc) | hr | 40
2.1.6 |  | Pipe layer | hr | 12
2.1.7 |  | Semi Skilled Labourer | hr | 40
2.1.8 |  | Unskilled Labour | hr | 40
2.1.9 |  | Security guard | hr | 40
2.2 |  | Materials
2.2.1 |  | Allow for Materials | Sum | 1 | 20000 | 20000
2.2.2 |  | Overheads, charges and profit on item 2.2.1 | % | 20000
2.3 |  | Plant (rates include establishments)
2.3.1 |  | Front-end Loader, approx. flywheel power 145 kW | hr | 20
2.3.2 |  | Back acting excavator, approx. flywheel power 100 kW | hr | 20
2.3.3 |  | Hand vibrating compactor, static mass | hr | 12
2.3.4 |  | Mobile Crane, 5 tonne at 3m radius | hr | 12
2.3.5 |  | Compressor, 10.3 m3/min including tools and hoses | hr | 16
2.3.6 |  | Poker vibrator | hr | 12
2.3.7 |  | Concrete Mixer 0.3 m3 dry mix capacity | hr | 16
2.3.8 |  | 40m3/hour Water Pump including layflat hoses | hr | 320
2.3.9 |  | Tipper, 10 m3 capacity | hr | 24
2.3.10 |  | Tipper, 5 m3 capacity | hr | 24
2.3.11 |  | Flat bed, 7 tonne capacity | hr | 24
2.3.12 |  | Flat bed, 5 tonne capacity | hr | 24
2.3.13 |  | 1 tonne LDV | hr | 24
TOTAL CARRIED FORWARD TO SUMMARY

## Inlet works
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200 C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 3: INLET WORKS
Item Ref | Payment Refers SANS | Description | Unit | Qty | Rate | Amount
SECTION 3: INLET WORKS
3.1 | 1200 C | SITE CLEARANCE
3.1.1 | 8.2.1 | Clear and grub | m2 | 10
3.1.2 | 8.2.8 | Demolish and remove structure, buildings and dismantle steelwork etc. (adjacent to the existing inlet works channel) | Sum | 1
3.1.3 | 8.2.9 | Cart materials and debris and dump within closest disposal site (Provisional) | t.km | 2
3.1.4 | 8.2.10 | Remove Topsoil to Nominal Depth 150 mm (or other Stated Depth), Stockpile,and Maintain | m2 | 10
3.1.5 |  | Saw cut the existing inletworks concrete to make provision for the 1000 mm wide and 600 mm deep bypass channel of 3m length | Sum | 1
3.2 | 1200 D | EARTHWORKS
| 8.3.2 | Bulk excavations
a) i) Excavate in all materials, compact formation and use material for embankment or backfill or dispose, as ordered :
Exceeding but Not Exceeding
3.2.1 |  | .01) 0.0 m 1.0 m | m³ | 4
3.2.2 |  | .02) 1.0 m 2.0 m | m³ | 4
3.2.3 |  | .03) 2.0 m 3.0 m | m³ | 4
3.2.4 |  | .04) 3.0 m 4.0 m | m³ | 4
b) Extra over items 8.3.2a) above for:
3.2.5 |  | ii) Hard rock materials | m³ | 6
| 8.3.4 | Importing of materials
a) Extra-over for importation of materials from commercial sources
3.2.6 |  | i) 150mm G5 natural material compacted to 95% Mod AASHTO for laying inside the pond | m³ | 1
3.2.7 |  | ii) 150mm G7 or better natural material compacted to 93% Mod AASHTO for laying inside the pond | m³ | 1
3.2.8 | 8.3.8.1 | Existing services
3.2.9 |  | c) Excavate by hand in soft material to expose services | P/Sum | 1 | 10000 | 10000
3.2.10 | 8.3.8.2 | Dealing with services that are at risk because of the construction of earthworks (Provisional) | P/Sum | 1 | 20000 | 20000
3.2.11 | 8.3.9 | Extra-over for backfill or fill material against structures (Provisional) | m³ | 5
3.3 | 1200 G | Concrete (STRUCTURAL) - Chambers
| 8.2 | Formwork
| 8.2.2 | Smooth, vertical, plane to:
3.3.1 |  | walls | m² | 30
3.3.2 |  | slab | m² | 3
3.3.3 |  | Plinth | m² | 3
| 8.2.6 | Box out holes/Form voids
3.3.4 |  | a) Circular opening for outside diameter pipe up to and including 300 mm NB through walls of thickness: | No | 1
3.3.5 |  | d) weir | No | 1
| 8.3 | Reinforcement
3.3.6 | 8.3.1 | High tensile Steel with diameters rangining from 8mm up to 32 mm | t | 2.45
| 8.4 | Concrete
| 8.4.1 | Strength Concrete Grade 35 MPa/19 mm to:
3.3.7 |  | walls | m³ | 10
3.3.8 |  | slab | m³ | 2
3.3.9 |  | Plinth | m³ | 2
3.3.10 | 8.4.2 | Blinding layer in Class 15/19 concrete, 50mm thickness | m² | 10
| 8.4.4 | Unformed Surface Finishes
| a) | Wood-floated finish to:
3.3.11 |  | walls | m² | 3
3.3.12 |  | slab | m² | 5
3.3.13 |  | Plinth | m² | 5
TOTAL CARRIED TO SUMMARY

## BNR
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 4: BNR
Item Ref | Payment Refers SANS | Description | Unit | Qty | Rate | Amount
SECTION 4: BNR
4.1 | 1200 C | SITE CLEARANCE
4.1.1 | 8.2.1 | Clear and grub | m2 | 1605
4.1.2 | PSC 8.2.1.1 | Drain the wastewater from the existing earation tank and discharge it into the existing pond and by pass the the aeration tank for the duration of new BNR construction | m3 | 4500
4.1.3 | PSC 8.2.1.2 | High pressure wash (water jet) the interior walls and bottom of the oxidation ditch | m² | 2000
4.1.4 |  | Clean and remove all settled grit, sand and organic matter at the bottom of the aeration tank | m3 | 40
4.1.5 | 8.2.4 | Reclear surfaces (provisional) (where ordered by Engineer) | m2 | 100
4.1.6 | 8.2.8 | Demolish and remove structure, buildings and dismantle steelwork etc. (adjacent to the existing aeration tank) | Sum | 1
4.1.7 | 8.2.9 | Cart materials and debris and dump within closest disposal site (Provisional) | t.km | 10
4.1.8 | 8.2.10 | Remove Topsoil to Nominal Depth 150 mm (or other Stated Depth), Stockpile,and Maintain | m2 | 250
4.2 | 1200 D | EARTHWORKS
| 8.3.2 | Bulk excavations
a) i) Excavate in all materials, compact formation and use material for embankment or backfill or dispose, as ordered :
Exceeding but Not Exceeding
4.2.1 |  | .01) 0.0 m 1.0 m | m³ | 7
4.2.2 |  | .02) 1.0 m 2.0 m | m³ | 12
4.2.3 |  | .03) 2.0 m 3.0 m | m³ | 1800
4.2.4 |  | .04) 3.0 m 4.0 m | m³ | 885
4.2.5 |  | .05) 4.0 m 5.0 m | m³ | 1325
4.2.6 |  | .06) 5.0 m 6.0 m | m³ | 450
4.2.7 |  | ii) Excavate in all materials for the subsoil water drainage and hydrostatic pressure management to a depth not exceeding 4.5m and stockpile on site for use later | m³ | 100
b) Extra over items 8.3.2a) above for:
4.2.9 |  | ii) Hard rock materials | m³ | 1800
| 8.3.4 | Importing of materials
a) Extra-over for importation of materials from commercial sources
4.2.10 |  | i) 300mm G5 natural material compacted to 95% Mod AASHTO for laying inside the pond | m³ | 335
4.2.11 |  | ii) 300mm G7 or better natural material compacted to 93% Mod AASHTO for laying inside the pond | m³ | 335
4.2.12 | a) | Services that intersect a trench | No | 5
4.2.13 | b) | Services that adjoin a trench | m | 10
4.2.14 | 8.3.7 | Additional lateral support between 1m to 2.5m deep (Provisional) for ensuring the stability of the excavation adjacent to the existing tank | P/Sum | 1 | 150000 | 150000
| 8.3.8.1 | Existing services
4.2.15 |  | c) Excavate by hand in soft material to expose services | P/Sum | 1 | 15000 | 15000
4.2.16 | 8.3.8.2 | Dealing with services that are at risk because of the construction of earthworks (Provisional) | P/Sum | 1 | 20000 | 20000
4.2.17 | 8.3.9 | Extra-over for backfill or fill material against structures (Provisional) | m³ | 10
CARRIED FORWARD
BROUGHT FORWARD
4.3 | 1200 G | Concrete (STRUCTURAL) - New BNR
| 8.2 | FORMWORK
| 8.2.2 | Smooth, vertical, plane to:
4.3.1 |  | Vertical curved around outside perimeter of column | m² | 145
4.3.2 |  | walls | m² | 3600
4.3.3 |  | walkway | m² | 810
4.3.4 |  | slab | m² | 75
4.3.5 |  | Channel | m² | 11
| 8.2.5 | Narrow widths (up to 300 mm)
| 8.2.6 | Box out Holea/ form voids
Casting of pipes/specials into concrete for:
a) Pipes up to and including 350 mm NB through walls of thickness:
Over (m) Up to and incl (m)
4.3.6 |  | 0.00 0.5 | No | 10
4.3.7 |  | Cable sleeves through walls | m | 20
4.4 | 8.3 | REINFORCEMENT
4.4.1 | 8.3.1 | High tensile Steel with diameters rangining from 8mm up to 32 mm | t | 186
4.4.2 | 8.3.2 | High-tensile Welded Mesh type:Ref 395 in standard sheets for the channel | m² | 46
4.5 | 8.4 | CONCRETE
| 8.4.1 | Strength Concrete Grade 35 MPa/19 mm to:
4.5.1 |  | walls | m³ | 360
4.5.2 |  | walkway | m³ | 130
4.5.3 |  | slab | m³ | 440
4.5.4 |  | column | m³ | 12
Strength Concrete Grade 25 MPa/19 mm to:
4.5.5 |  | V-channels around perimeter of the BNR tank | m³ | 8
4.5.6 | 8.4.2 | Blinding layer in Class 15/19 concrete, 50mm thickness | m³ | 60
4.5.7 | 8.4.3 | 50mm thick sand cement (1:3) floor screeds with falls including V-joints to form panels with smooth steel trowelled finish to top average 35mm thick to floors | m³ | 60
| 8.4.3 | No-fines concrete layer:
Under tank floor and around drains pipes for the following:
4.5.8 |  | Construction joint | m² | 20
4.5.9 |  | Contraction joint | m² | 20
4.5.10 |  | Underdrain | m² | 2
| 8.4.4 | Unformed Surface Finishes
| a) | Wood-floated finish to:
4.5.11 |  | walls | m² | 227
4.5.12 |  | walkway | m² | 3370
4.5.13 |  | slab | m² | 1200
4.5.14 |  | column | m² | 5
4.5.15 |  | V-channel | m² | 46
| b) | Steel-floated finish to:
4.5.16 |  | screed | m² | 1200
4.6 | 8.5 | JOINTS
4.6.1 | PSG 8.5.1 | Contraction joints between floor, complete with flexijoint filler and 250mm rearguard "S" waterbar | m | 100
4.6.2 |  | Vertical Construction joint with 200mm Hyperlon bandage strip, backing bond breaker, 350mm wide and Kuniseal Waaterstop or similar approved product and reinforcement in wall. | m | 540
4.6.3 |  | 1,6mm thick and 200mm wide galvanised Steel Waterstops for use in construction joints in tank | m | 100
4.6.4 |  | Construction joints between floor, complete with 100mm high keyed joint and 250mm rearguard "S" waterbar | m | 100
4.7 | 1200 H | STRUCTURAL STEELWORK
| 8.3.7 | Handrails
4.7.1 |  | a) GRP Handrail assembly complete as pe the drawing | Sum | 1
4.7.2 | 8.3.8 | HDG stairs, complete and installed | No. | 4
| 8.3.9 | Flooring, complete and installed with frames for:
4.7.2 |  | a) Supply and install 38x38mm square mesh pattern, 38mm Deep open grid floor anti-slip grey coloured fibre glass grating, complete with the fixing components | m2 | 60
4.7.3 | 8.3.10 | Non-destructive Testing (Provisional) | Hr | 120
4.7.4 | 8.3.13 | Corrosion Protection, extra over items 8.2.1 to 8.3.9 | Sum | 1
CARRIED FORWARD
BROUGHT FORWARD
4.8 |  | Miscellaneous
| PSLB 8.2.6 | Sub-soil drainage
4.8.1 |  | Pitch-fibre pipes and fittings complete with couplings 110 mm internal diameter, perforated | m | 100
4.8.2 |  | Supply and installation of Geofabric filter material (BIDIM Grade A4 or similar) around stone | m² | 10
4.8.3 |  | 250 micron DPC between floor and no-fines concrete | m² | 200
4.8.4 | PSG 8.9.1 | Supply and Install 0,25 mm thick HDPE lining underneath the channel. | m2 | 46
4.8.5 | PSG 8.9.2 | Supply and install Goundwater relief valve diameter 110mm and flow rate of 90 litres/minute | No. | 20
4.8.6 | PSG 8.9.3 | Water Tightness Testing | Sum | 1
4.9 |  | Concrete repairs on existing aeration tank
column
4.9.1 |  | Repair and seal the concrete. Chip open spalled and cracks (up to 10 mm wide) to sound concrete, apply approved bonding slurry and anti-corrosion coating to exposed reinforcement | m2 | 50
4.9.2 |  | Apply cementitious concrete repair mortar to maximum depth of 35 mm or as per manufactures specification to all cleaned spalled concrete in the existing. | m2 | 30
4.9.3 |  | Coat the interior of all cleaned and repaired concrete works with penetrating corrossion inhibitor as per manuactures specifications | m2 | 30
Floor joints
4.9.4 |  | Remove any existing joint sealant to form a level surface between adjoining slabs | m | 50
4.9.5 |  | Grind the concrete on each side of the joint to a smooth level surface. | m | 50
4.9.6 |  | Apply a 150mm wide flexible modified polyolefin waterproofing bandage to joints and fix in place with approved thixotropic epoxy adhesive with at least 5 MPa one day bond strength. As per manufacturer's specifications. | m | 50
Wall
4.9.7 |  | Coat wall with penetrating concrete protective treatment | m² | 20
4.9.8 |  | Coat vertical cracks with styrene/butadiene copolymer latex suitable for use on concrete surfaces including neccesary surface treatment as per manufacturer's specification. 30mm total width. As per manufacturer's specifications. | m | 30
4.9.9 |  | Remove existing wall joint sealant . | m | 15
4.9.10 |  | Apply a 150mm wide flexible modified polyolefin waterproofing bandage to wall joints and fix in place with approved thixotropic epoxy adhesive with at least 5 MPa one day bond strength. As per manufacturer's specifications. | m | 30
PIPELINES
4.10.0 | 1200 DB | Earthworks
| 8.3.2.a | Excavate in all materials for trenches, backfill and compact to 93% Mod AASHTO Density, including disposal of surplus and unsuitable material as directed for :
Pipes up to 600mm dia for the following depths:
Exceeding but Not Exceeding
4.10.1 |  | .01) 1.0 m 2.0 m | m³ | 140
| 8.3.2.b | Extra-over item (from 1.2.1 to 1.2.2) above for:
4.10.2 |  | .01) Intermediate excavation | m³ | 8
4.10.3 |  | .02) Hard rock excavation | m³ | 3
4.10.4 | 8.3.2 c | Excavate and dispose of unsuitable material from trench bottom (Provisional) | m³ | 5
| 8.3.3 | Excavation ancillaries
| 8.3.3.1 | Make up deficiency in backfill material (Provisional )
4.10.5 |  | .01) From other necessary excavations on site | m³ | 10
4.10.6 |  | .02) by importation from commercial | m³ | 5
4.10.7 | 8.3.4 | a) Shore trench opposite structures or services | m | 46
4.10.8 |  | b) Temproray works | Sum | 1
4.10.9 | 8.3.5 | Existing serives that intersect or adjoin a pipe trench | m | 5
4.11.0 | 1200 LB | Bedding
| 8.3.2.3 | Supply only of bedding by Importation from Commercial Source
4.11.1 |  | a) Selected granular material | m³ | 30
4.11.2 |  | b) Selected fill material | m³ | 50
CARRIED FORWARD
BROUGHT FORWARD
4.12.0 | 1200 L | Medium-Pressure Pipelines
| 8.2.1 | Supply, lay, join, bed, test and disinfect pipes all the pipe works complete with the couplings as per the drawing
4.12.1 |  | .01) 315mm uPVC Class 12 | m | 60
4.12.2 |  | .01) 250mm uPVC Class 12 | m | 68
| 8.2.2 | Pipe specials
Extra-over Items 3.4 for supplying, laying and bedding of specials complete with couplings for:
a) Fabricated fittings for PVC bends Class 12
45o
4.12.3 |  | 315 mm dia spigot/socket bend | No | 2
4.12.4 |  | 250 mm dia spigot/socket bend | No | 2
90o
4.12.5 |  | 315 mm dia | No | 4
4.12.6 |  | 250 mm dia | No | 4
| 8.2.5 | Supply and place pipes, valves and specials
Mild Steel pipes inside PN10
a) Inlet Structure pipework (from Head of Works):
4.12.7 |  | NB350 special pipe. NB350 straight pipe, 470mm long plain ended on one end and on the other end welded to a 90° short radius bend, flanged on one side. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.8 |  | NB350 puddle flange piece flanged on both ends, 785.1mm long with the puddle flange centrally located. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.9 |  | Special pipe. NB350 straight pipe, 800mm long flanged on one end and on the other end welded with a 90° short radius bend, flanged on one side. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.10 |  | NB350 straight pipe, 1746mm long flanged on both ends. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.11 |  | NB350 90° short radius bend flanged on both ends. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.12 |  | NB350 straight pipe, 500mm long flanged on both ends. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.13 |  | Viking Johnson or similar flange adapter to suit 350NB uPVC from steel pipe | No | 1
4.12.14 |  | NB 315 uPVC straight pipe spigot & socket on both ends, Class 12 | No | 1
a) Inlet Structure pipework (from Return Activated Sludge):
4.12.15 |  | Special pipe. NB350 straight pipe, 1803mm long plain ended on one end and on the other end welded to a 90° short radius bend, flanged on one side. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.16 |  | NB250 puddle flange piece flanged on both ends, 501 mm long with the puddle flange centrally located. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.17 |  | Special pipe. NB250 straight pipe, 1640mm long flanged on one end and on the other end welded with a 90° short radius bend, flanged on one side. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.18 |  | NB250 straight pipe, 1329 mm long flanged on both ends. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.19 |  | NB250 90° short radius bend flanged on both ends. All flanges to SANS 1123, Table 1000/3 | No | 2
4.12.20 |  | NB250 straight pipe, 500mm long flanged on both ends. All flanges to SANS 1123, Table 1000/3 | No | 1
4.12.21 |  | Viking Johnson or similar flange adapter to suit 250NB uPVC from steel pipe | No | 1
4.12.22 |  | NB 250 uPVC straight pipe spigot & socket on both ends, Class 12 | No | 1
4.12.23 | DS 3, MCP 1 | NB350 Insulation Flange Kits - Supply Insulation Flange Kits | No. | 1
4.12.24 |  | NB250 Insulation Flange Kits - Supply Insulation Flange Kits | No. | 1
4.12.25 | PSL 8.2.15 | Supply and apply an anti-corrosion and sealing tape based on a synthetic fabric, impregnated and coated with a neutral petrolatum compound, on a 350mm mild steel pipe for 1100m long. | Sum | 1
TOTAL CARRIED TO SUMMARY

## Secondary Settling Tank
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 5: SECONDARY SETTLING TANK
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
5 |  | SECTION 5: SECONDARY SETTLING TANK
| 1200 C | SITE CLEARANCE
|  | High pressure wash (water jet) the interior walls, bottom and launder of the Secondary Settling Tank | m² | 655
|  | Drain the wastewater from the Settling tank and discharge it into the existing oxidation ponds | m3 | 1400
|  | Clean and remove all settled grit, sand and organic matter at the bottom of the Secondary Settling Tank | m3 | 29
| 8.2.9 | Cart materials and debris removed from the Settling Tank and dispose within the Wastewater Treatment works site | m3 | 29
| 1200 D | EARTHWORKS
| 8.3.1.2 | Remove topsoil to nominal depth of 150mm to stockpile and maintain | m2 | 3
| 8.3.2 | a) Excavate in all materials for the subsoil water drainage and hydrostatic pressure management to a depth not exceeding 4.5m and stockpile on site for use later | m³ | 100
|  | b) Extra over item above for hard rock excavation | m³ | 3
4.9 |  | Concrete repairs on existing sst
column
4.9.1 |  | Repair and seal the concrete. Chip open spalled and cracks (up to 10 mm wide) to sound concrete, apply approved bonding slurry and anti-corrosion coating to exposed reinforcement | m2 | 50
4.9.2 |  | Apply cementitious concrete repair mortar to maximum depth of 35 mm or as per manufactures specification to all cleaned spalled concrete in the existing. | m2 | 30
4.9.3 |  | Coat the interior of all cleaned and repaired concrete works with penetrating corrossion inhibitor as per manuactures specifications | m2 | 30
Floor joints
4.9.4 |  | Remove any existing joint sealant to form a level surface between adjoining slabs | m | 50
4.9.5 |  | Grind the concrete on each side of the joint to a smooth level surface. | m | 50
4.9.6 |  | Apply a 150mm wide flexible modified polyolefin waterproofing bandage to joints and fix in place with approved thixotropic epoxy adhesive with at least 5 MPa one day bond strength. As per manufacturer's specifications. | m | 50
Wall
4.9.7 |  | Coat wall with penetrating concrete protective treatment | m² | 20
4.9.8 |  | Coat vertical cracks with styrene/butadiene copolymer latex suitable for use on concrete surfaces including neccesary surface treatment as per manufacturer's specification. 30mm total width. As per manufacturer's specifications. | m | 30
4.9.9 |  | Remove existing wall joint sealant . | m | 15
4.9.10 |  | Apply a 150mm wide flexible modified polyolefin waterproofing bandage to wall joints and fix in place with approved thixotropic epoxy adhesive with at least 5 MPa one day bond strength. As per manufacturer's specifications. | m | 30
TOTAL CARRIED FORWARD TO SUMMARY

## RAS
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 6: RAS STATION
Item Ref | Payment Refers SANS | Description | Unit | Qty | Rate | Amount
SECTION 6: RAS STATION
6.1 | 1200 C | Site Clearance
6.1.1 | 8.2.1 | Clear and grub | m2 | 20
6.1.2 | 8.2.8 | Demolish and remove structure, buildings and dismantle steelwork etc. | Sum | 1
6.1.3 | 8.2.9 | Cart materials and debris and dump to the neareste municipal waste (Provisional) | t.km | 5
6.1.4 | 8.2.10 | Remove Topsoil to Nominal Depth 150 mm (or other Stated Depth), Stockpile,and Maintain | m³ | 4
6.2 | 1200 D | EARTHWORKS
| 8.3.2 | Bulk excavations
6.2.1 |  | a) i) Excavate in all materials, compact formation and use material for embankment or backfill or dispose, as ordered : | m³ | 8
b) Extra over items 8.3.2a) above for:
6.2.2 |  | i) Intermediate materials | m³ | 0.5
6.2.3 |  | ii) Hard rock materials | m³ | 0.3
| 8.3.4 | Importing of materials
a) Extra-over for importation of materials from commercial sources
6.2.4 |  | i) 150mm G7 or better natural material compacted to 93% Mod AASHTO | m³ | 5
6.2.5 |  | i) 150mm G5 or better natural material compacted to 93% Mod AASHTO | m³ | 5
6.2.6 | 8.3.8.2 | Dealing with services that are at risk because of the construction of earthworks (Provisional) | P/Sum | 1 | 10000 | 10000
6.3 | 1200 G | CONCRETE (STRUCTURAL) - Chamber
| 8.2 | FORMWORK
| 8.2.2 | Smooth, vertical, plane to:
6.3.1 |  | Plinth | m² | 1
6.3.2 |  | slab | m² | 6
| 8.2.5 | Narrow widths (up to 300 mm)
Smooth, vertical, plane to:
Casting of pipes/specials into concrete for:
Pipes up to and including 350 mm NB through walls of thickness:
Over (m) Up to and incl (m)
6.3.3 |  | 0.00 0.35 | No | 3
6.3.4 |  | Cable sleeves through walls | m | 1
6.4 | 8.3 | REINFORCEMENT
6.4.1 | 8.3.1 | High tensile Steel with diameters rangining from 8mm up to 32 mm | t | 1.3
6.4.2 | 8.3.2 | High-tensile Welded Mesh type:Ref 395 in standard sheets to surface beds and ramp | m² | 20
6.5 | 8.4 | CONCRETE
| 8.4.1 | Strength Concrete Grade 30 MPa/19 mm to:
6.5.1 |  | cover | m³ | 6.5
6.5.2 |  | slab | m³ | 0.5
| 8.4.4 | Unformed Surface Finishes
| a) | Wood-floated finish to:
6.5.2 |  | Top of surface beds | m² | 20
6.5.3 |  | Top of plinth | m² | 2
| 8.5 | JOINTS
Expansion joints:
6.5.4 |  | 12 mm thick joint filler, vertical along edge of surface bed, raked out for a depth of 20 mm and sealed with approved polyurethane sealant | m | 5
CARRIED FORWARD
BROUGHT FORWARD
6.6 | 1200 HA | STRUCTURAL STEELWORK (SUNDRY
|  | Steel Cage support to protect the pumps, complete with fixers as per the drawings. | Sum | 1
| 1200 L and MPW10 | Medium-Pressure Pipelines
6.6.1 | 8.2.1 | a) Supply handle, lay and bed pipes on flexible pipe bedding complete with coupling, testing and disinfecting
6.6.2 |  | 250ND uPVC straight pipe spigot & socket on both ends, Class 9 | m | 18
6.6.3 |  | 250ND Mild steel straight pipe with flanges on both ends, all flanges to sans 1123, table 1000/3 | m | 1
6.6.4 |  | 250ND Mild steel straight pipe with flanges on both ends, all flanges to sans 1123, table 1000/3 | m | 10
6.6.5 |  | 250ND straight HDPE pipe, PN10, butt welding pipe joint | m | 11
6.6.6 |  | 250ND Mild steel straight pipe with flanges on both ends, all flanges to sans 1123, table 1000/3 | m | 0.5
| 8.2.2 | Pipe specials
Extra-over Items (from 1.4.1 to 1.4.2) for supplying, laying and bedding of specials PVC-u bends Class 16 complete with couplings for:
6.6.7 |  | 315ND to 250ND HDPE Short spigot concentric reducer PE100, butt weld fabricated fitting | No | 2
6.6.8 |  | 250ND 45° HDPE sweep bend PE 100 , butt weld fabricated fitting | No | 2
6.6.9 |  | 250ND 90° short radius bend flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 4
6.6.10 |  | 250ND to 100nb reducer flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 2
6.6.11 |  | 250ND 90° short radius bend flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 10
6.6.12
6.6.13 |  | 250ND sweep tee flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 1
6.6.14 |  | viking johnson or similar flange adapter to suit 250ND uPVC pipe | No | 2
6.6.15 |  | viking johnson or similar flange adapter to suit 250ND steel to HDPE pipe | No | 2
6.6.16 |  | 250ND 22.5° plain spigot/socket bend , class 16 | No | 1
TOTAL CARRIED TO SUMMARY

## Sludge PONDS
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 7: SLUDGE DAMS
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
7 |  | SECTION 7: SLUDGE DAMS
7.1 | 1200 C | SITE CLEARANCE
7.1.2 |  | Clean and remove all material and debris within the narrow inlet channel width not exceeding 500 mm and 700 mm deep | m | 30
|  | Remove all the sand and gravel in the sludge drying beds and disposed of at the local domestic waste landfill | m3 | 25500
7.2 | 1200 HA | STRUCTURAL STEELWORK AND OTHER METAL WORK
7.2.2 |  | Refurbish all the existing mild steel handstop at the inlet of the sludge drying beds | No | 4
7.2.3 |  | clean all the pipelines between the BNR, SSTs and the Sludge dams. Pipeline to be sand blasted and lined | sum | 1
TOTAL CARRIED FORWARD TO SUMMARY
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: CHECK WITH DANIEL ON THE LAYERWORKS

## Chlorine Building
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 8: CHLORINE BUILDING
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
8. |  | SECTION 8: CHLORINE BUILDING
8.1 | 1200 C | SITE CLEARANCE
8.1.1 | 8.2.1 | Clear and grub | ha | 0.01
8.1.2 | 8.2.9 | Cart materials and debris and dump at the disposal site provided by the contractor(Provisional) | t.km | 10
8.1.3 | 8.2.10 | Remove Topsoil to Nominal Depth 150 mm (or other Stated Depth), Stockpile,and Maintain | m³ | 10
8.2 | SPEC | BUILDING WORK
Doors and windows (including frames and glass)
8.2.1 |  | 914x2438mm Steel Transformer door and frame, Type H, including brass ironmongery and locks as per design specification | No | 3
8.2.2 |  | 2200x3840mm Steel Transformer door and frame, Type YV, including brass ironmongery and locks as per design specification | No | 1
8.2.3 |  | 1500mm wide x 730mm high bronze anodised aluminium frame and smart glass as per design specification | No | 2
8.2.4 |  | 500mm wide x 730mm high bronze anodised aluminium frame and smart glass as per design specification | No | 1
8.2.5 |  | 1200mm wide x 960mm high bronze anodised aluminium frame and clear safety glass | No | 1
FIRE APPLIANCES ETC
8.2.6 |  | Everyway or similar hose reel complete with 30m plastic hose, chromium plated stopcock, shut-off nozzle and wall bracket | No | 1
8.2.7 |  | 4,5kg Dry chemical fire extinguisher | No | 2
Grating
8.2.8 |  | 38x38mm square mesh pattern, 38mm Deep open grid anti-slip grey coloured fibre glass grating, complete with the fixing components | m² | 12
8.3 |  | PAINTWORK
PAINTWORK ETC TO EXISTING WORKS
8.3.1 |  | Scrape the existing paint on the walls and prepare the surface for new paint | m² | 70
PAINTWORK ETC TO NEW WORK
ON FLOATED PLASTER
One coat universal undercoat and two coats interior quality super acrylic PVA paint
8.3.2 |  | On internal plastered walls | m² | 70
8.3.3 |  | On internal plastered ceilings and beams | m² | 18
One coat pigmented primer and two coats interior non drip enamel paint
8.3.4 |  | On internal plastered walls | m² | 70
ON METAL
Spot priming defects in pre-primed surfaces with zinc chromate primer and applying one universal undercoat and two coats non drip high gloss alkyd enamel paint on steel
8.3.5 |  | On doors and frames | m² | 20
TOTAL CARRIED TO SUMMARY

## Wash Water Pumps
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 9: WASH WATER SYSTEM
Item Ref | Payment Refers SANS | Description | Unit | Qty | Rate | Amount
9 |  | SECTION 9: WASH WATER SYSTEM
PUMPS
9.1 | 1200 C | Site Clearance
9.1.1 | 8.2.1 | Clear and grub | m2 | 20
9.1.2 | 8.2.8 | Demolish and remove structure, buildings and dismantle steelwork etc. | Sum | 1
9.1.3 | 8.2.9 | Cart materials and debris and dump to the neareste municipal waste (Provisional) | t.km | 2
9.1.4 | 8.2.10 | Remove Topsoil to Nominal Depth 150 mm (or other Stated Depth), Stockpile,and Maintain | m³ | 2
9.2 | 1200 D | EARTHWORKS
| 8.3.2 | Bulk excavations
9.2.1 |  | a) i) Excavate in all materials, compact formation and use material for embankment or backfill or dispose, as ordered : | m³ | 14
9.2.2 |  | b) Extra over items 8.3.2a) above for:
9.2.3 |  | i) Intermediate materials | m³ | 0.7
9.2.4 |  | ii) Hard rock materials | m³ | 0.3
| 8.3.4 | Importing of materials
a) Extra-over for importation of materials from commercial sources
9.2.5 |  | i) 150mm G7 or better natural material compacted to 93% Mod AASHTO | m³ | 6
9.2.6 |  | i) 150mm G5 or better natural material compacted to 93% Mod AASHTO | m³ | 5
9.2.7 | 8.3.8.2 | Dealing with services that are at risk because of the construction of earthworks (Provisional) | P/Sum | 1 | 10000 | 10000
CARRIED FORWARD
BROUGHT FORWARD
9.3 | 1200 L and MPW10 | Medium-Pressure Pipelines
| 8.2.1 | a) Supply handle, lay and bed pipes on flexible pipe bedding complete with coupling, testing and disinfecting
9.3.1 |  | 100ND uPVC straight pipe spigot & socket on both ends, Class 9 | m | 18
9.3.2 |  | 100ND Mild steel straight pipe with flanges on both ends, all flanges to sans 1123, table 1000/3 | m | 1
9.3.3 |  | 100ND Mild steel straight pipe with flanges on both ends, all flanges to sans 1123, table 1000/3 | m | 10
9.3.4 |  | 100ND straight HDPE pipe, PN10, butt welding pipe joint | m | 11
9.3.5 |  | 100ND Mild steel straight pipe with flanges on both ends, all flanges to sans 1123, table 1000/3 | m | 0.5
| 8.2.2 | Pipe specials
Extra-over Items (from 1.4.1 to 1.4.2) for supplying, laying and bedding of specials PVC-u bends Class 16 complete with couplings for:
9.3.6 |  | 100ND to 110ND HDPE Short spigot concentric reducer PE100, butt weld fabricated fitting | No | 2
9.3.7 |  | 110ND 45° HDPE sweep bend PE 100 , butt weld fabricated fitting | No | 2
9.3.8 |  | 100ND 90° short radius bend flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 4
9.3.9 |  | 110ND to 100nb reducer flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 2
9.3.10 |  | 110ND 90° short radius bend flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 10
9.3.11 |  | 110ND sweep tee flanged on both ends. all flanges to sans 1123, table 1000/3 | No | 1
9.3.12 |  | viking johnson or similar flange adapter to suit 110ND uPVC pipe | No | 2
9.3.13 |  | viking johnson or similar flange adapter to suit 110ND steel to HDPE pipe | No | 2
9.3.14 |  | 110ND 22.5° plain spigot/socket bend , class 16 | No | 1
ELEVATED TOWER
9.4 | 1200 C | SITE CLEARANCE
9.4.1 | 8.2.1 | Clear and grub | m² | 15
9.4.2 | 8.2.10 | Remove Topsoil to Nominal Depth 150 mm (or other Stated Depth), Stockpile,and Maintain | m³ | 3
9.4.3 | 1200 D | EARTHWORKS
9.4.4 | 8.3.2 | Bulk excavations
9.4.5 |  | a) i) Excavate in all materials, compact formation and use material for embankment or backfill or dispose, as ordered : | m³ | 5
9.4.6 |  | b) Extra over items 8.3.2a) above for:
9.4.7 |  | i) Intermediate materials | m³ | 0.4
9.4.8 |  | ii) Hard rock materials | m³ | 0.1
| 8.3.4 | Importing of materials
a) Extra-over for importation of materials from commercial sources
9.4.9 |  | i) 150mm G7 or better natural material compacted to 93% Mod AASHTO for laying inside the pond | m³ | 5
9.4.10 | 8.3.8.2 | Dealing with services that are at risk because of the construction of earthworks (Provisional) | P/Sum | 1
9.5 | 1200 G | CONCRETE (STRUCTURAL)
| 8.2 | FORMWORK
| 8.2.2 | Smooth, vertical, plane to:
9.5.1 |  | Plinth | m² | 3
9.5.2 |  | Column Base | m² | 8
9.5.3 |  | Column Stub | m² | 10
9.5.4 |  | Slab | m² | 3
9.6 | 8.3 | REINFORCEMENT
9.6.1 | 8.3.1 | High tensile Steel with diameters rangining from 8mm up to 32 mm | t | 0.5
9.6.2 | 8.3.2 | High-tensile Welded Mesh type:Ref 395 in standard sheets to surface beds and ramp | m² | 10
9.7 | 8.4 | CONCRETE
| 8.4.1 | Strength Concrete Grade 25 MPa/19 mm to:
9.7.1 |  | Plinth | m³ | 1
9.7.2 |  | Column Base | m³ | 3
9.7.3 |  | Column Stub | m³ | 2
9.7.4 |  | Slab | m³ | 2
CARRIED FORWARD
BROUGHT FORWARD
| 8.4.4 | Unformed Surface Finishes
| a) | Wood-floated finish to:
9.7.5 |  | Top of bases | m² | 10
9.7.6 |  | Top of plinth | m² | 3
| b) | Steel-floated finish to:
9.7.7 |  | Top of surface beds | m² | 10
9.8 | 8.5 | JOINTS
Expansion joints:
9.8.1 |  | 12 mm thick joint filler, vertical along edge of surface bed, raked out for a depth of 20 mm and sealed with approved polyurethane sealant | m | 4
9.9 | 1200 H | STRUCTURAL STEELWORK
9.9.1 | 8.3.1.1 | Preparation of shop detail drawings | Sum | 1
9.9.2 | 8.3.1.2 | Supply and fabrication of steelwork | t | 2
9.9.3 | 8.3.2 | Delivery to site | t | 0.18
9.9.4 | 8.3.3 | Erection on site | t | 0.18
9.9.5 | 8.3.4 | Erection bolts, M16 | No | 160
9.9.6 | 8.3.5 | Site Welding | m | 3
9.9.7 | 8.3.6 | Holding down Bolts, M30 | No | 50
| 8.3.7 | Handrails
|  | a) Handrail assembly complete | Sum | 1
9.9.8 | 8.3.8 | ladder, complete and installed | No | 1
9.9.9 | 8.3.10 | Non-destructive Testing (Provisional) | Hr | 3
9.9.10 | 8.3.13 | Corrosion Protection, extra over items 8.2.1 to 8.3.9 | Sum | 1
CARRIED FORWARD
BROUGHT FORWARD
9.1 |  | PIPEWORK
| 1200 L | MEDIUM- PRESSURE PIPELINES
| 8.2.1 | a) Supply handle, lay and bed pipes on flexible pipe bedding complete with coupling, testing and disinfecting
9.10.1 |  | 110NB Mild steel straight pipe plain ended on both ends, | m | 30
9.10.2 |  | 110NB HDPE PN10 | m | 100
| 8.2.2 | Pipe specials
Extra-over Items (from 2.8.1 to 2.8.2) for supplying, laying and bedding of specials mild steel PN10 bends complete with couplings for:
9.10.3 |  | 110NB galvanised mild steel elbow F/F 90 degree | No | 20
9.10.4 |  | 110 NB galvanised mild steel equal tee | No | 6
9.10.5 |  | viking johnson or similar flange adapter to suit 110NB steel to HDPE pipe | No | 2
Miscellaneous
9.10.6 |  | Supply and delivery of 2,5kl water storage (Linear Low-density polyethylene) | No | 1
9.10.7 |  | Supply and insrall 38x38mm square mesh pattern, 38mm Deep open grid anti-slip grey coloured fibre glass grating, complete with the fixing components | m² | 6
TOTAL CARRIED TO SUMMARY

## Mechanical Works
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 10: MECHANICAL AND ELECTRICAL
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
10.1 |  | SECTION 10: MECHANICAL AND ELECTRICAL
PRELIMINARIES AND GENERALS - MECHANICAL
10.1.1 |  | Fixed portion | Sum | 1
10.1.2 |  | Time related portion | Sum | 1
10.1.3 |  | Co-operation and liason with Civil Contractor | Sum | 1
10.1.4 |  | Supervision | Month | 5
10.2 |  | INLET WORKS EQUIPMENT
10.2.1 | MFS 12.1 | Manufacture, Supply and delivery of mechanical front rake screens (25 mm openings) | No | 1
10.2.2 | MFS 12.2 | Installation, testing and commissioning of stainless steel mechanical front rake screens (25 mm opening) | No | 1
10.2.3 | DS 9 | Supply and delivery of 6m3 waste skips | No | 1
10.2.4 | MIA 10.3 and DS 10 | Manufacture, Supply and delivery of ultrasonic level detectors and flow meters | No | 1
10.2.5 | MIA 10.10 and DS10 | Installation, testing and commissioning of ultrasonic level detectors and flow meters | No | 1
10.2.6 |  | Remove the existing hand rake coarse screen, clean, refurbish and deliver to Municipal stores in Mogwase | No | 1
10.2.7 |  | Manufacture, Supply and delivery of 45 degree inclined fixed hand rake course screens (20 mm openings) to a 1050 mm wide channel and 650 mm deep channel | No | 1
10.2.8 |  | Installation, testing and commissioning of 45 degree inclined fixed course screens to a 1050 mm wide channel and 650 mm deep channel (20 mm openings) | No | 1
10.2.9 |  | Supply and delivery of two wheelbarrows (60 liter capacity) | No | 2
| MFC 10.3 and DS 15 | Manufacture, Supply and delivery of channel gates at the head of works to suit channel width and depth as follows: Width (mm) Depth (mm)
10.2.10 |  | 900 x 1000 | No | 2
10.2.11 |  | 600 x 1000 | No | 6
10.2.12 |  | 400 x 400 | No | 1
| MFC 10.3 and DS 15 | Refurbish, Installation, testing and commissioning of channel gates at the head of works to suit channel width and depth as follows: Width (mm) Depth (mm)
10.2.13 |  | 900 x 1000 | No | 2
10.2.14 |  | 600 x 1000 | No | 6
10.2.15 |  | 400 x 400 | No | 1
| MFC 10.7 and DS 15 | Installation, testing and commissioning of channel gates at the head of works to suit channel width and depth as follows: Width (mm) Depth (mm)
10.2.16 |  | 900 x 1000 | No | 2
10.2.17 |  | 600 x 1000 | No | 6
10.2.18 |  | 400 x 400 | No | 1
CARRIED FORWARD
BROUGHT FORWARD
| D16, MWP 22 | Lifting Pumps
Self priming pumps, complete with pump protections, manifolds valves and fittings and pipework supports for Head of Works Lift Pumping complete with motors, base plate and couplings
10.2.19 | MWP 22.1 | Manufacture, Supply and delivery | No | 2
10.2.20 | MWP 22.2 | Installation, testing and commissioning | No | 2
10.3 | DS13, DS15 | BIOLOGICAL REACTOR
2,5 kW mixers, complete with gearboxes, motors, connection manifold and all the required fittings for complete functional mixers
10.3.1 | MMA 8.1 and DS 11 | Design, manufacture, Supply and delivery of mixers | No | 8
10.3.2 | MMA 8.3 and DS 11 | Installation, testing and commissioning of mixers | No | 8
45 kW surface mounted aerator, complete with gearboxes, motors, manifolds and all required fittings for complete functional surface mounted aerators
10.3.3 | MMA 8.2 and DS 11 | Design, manufacture, Supply and delivery of surface mounted aerators | No | 2
10.3.4 | MMA 8.4 and DS 11 | Installation, testing and commissioning of surface mounted aerators | No | 2
55 kW surface mounted aerator, complete with gearboxes, motors, manifolds and all required fittings for complete functional surface mounted aerators
10.3.5 | MMA 8.2 and DS 11 | Design, manufacture, Supply and delivery of surface mounted aerators | No | 2
10.3.6 | MMA 8.4 and DS 11 | Installation, testing and commissioning of surface mounted aerators | No | 2
10.3.7 | MPW 15.1 | Design, Manufacture, Supply and delivery of 300 mm stainless steel sludge valves for the activated sludge recycle channel | No | 4
10.3.8 | MPW 15.2 | Installation, testing and commissioning of 300 mm stainless steel sludge valves for the activated sludge recycle channel | No | 4
10.3.9 | MPW 15.1 | Design, Manufacture, Supply and delivery of Flap gate valves for the activated sludge recycle to suite 1000 mm wide and 600 mm openings | No | 2
10.3.10 | MPW 15.2 | Installation, testing and commissioning of flap gate valves for the activated sludge recycle to suit 1000 mm by 600 mm deep openings | No | 2
Supply and delivery of the followings online instrumentation and sensors:
10.3.11 |  | a) pH probes (Aerobic tank) | No | 4
10.3.12 |  | b) Oxidation Reduction Potential (ORP) (Anaerobic, Anoxic and Aerobic tanks) | No | 4
10.3.13 |  | c) Dissolved Oxygen probes (Anaerobic, Anoxic and Aerobic tanks) | No | 4
Installation, testing and commissioning of the followings online instrumentation and sensors and terminate them in the existing MCC Building
10.3.14 |  | a) pH probes (Aerobic tank) | No | 4
10.3.15 |  | b) Oxidation Reduction Potential (ORP) (Anaerobic, Anoxic and Aerobic tanks) | No | 4
10.3.16 |  | c) Dissolved Oxygen probes (Anaerobic, Anoxic and Aerobic tanks) | No | 4
CARRIED FORWARD
BROUGHT FORWARD
10.4 | DS16, and MWP 22 | Pumps
Biological Nutrient Removal
Propeller-type pumps for activated sludge recycle in the biological reactor, complete with motors pump protections, manifolds, fittings, pipework supports, base plates and pump structure steel supports
10.4.1 | MWP 22.1 | Design, manufacture, Supply and delivery of propeller pumps | No | 2
10.4.2 | MWP 22.2 | Installation, testing and commissioning of propeller pumps | No | 2
Hoisting frame complete with hoist and chain for the propeller pumps
10.4.3 |  | Design, Manufacture, Supply and delivery | Sum | 1
10.4.4 |  | Installation, testing and commissioning | Sum | 1
10.5 |  | Return Activated Sludge (RAS) Pumps
Self priming pumps, complete with pump protections, manifolds valves and fittings and pipework supports for Return Activated Sludge Pumping complete with motors, base plate and couplings
10.5.1 | MWP 22.1 | Manufacture, Supply and delivery | No | 2
10.5.2 | MWP 22.2 | Installation, testing and commissioning | No | 2
10.5.3 |  | Refurbish, test and restore the existing RAS pumps and deliver to them to the Municipal Stores in Mogwase (and issue service certificates for the pumps) | No | 2
10.5.4 | MPW 15.1 | Manufacture, Supply and delivery of two 300 mm telescopic valves complete with platform mounted pedestal with handwheel | No | 2
10.5.5 | MPW 15.2 | Installation, testing and commissioning of two 300 mm telescopic valves complete with platform mounted pedestal with handwheel | No | 2
10.5.6 | DS15 | Remove and clean the existing telescopic valves and deliver them to Municipal stores in Mogwase | No | 2
| MPW 15 DS 15 | Valves
Extra-over Items 1.4 for supplying, laying and bedding of valves:
10.5.6 |  | 250ND handwheel cast iron (non-rising stem) resilient seal gate valve flanged on both ends. | No | 2
10.5.7 |  | 250ND handwheel cast iron (non-rising stem) resilient seal gate valve flanged on both ends. | No | 2
10.5.8 |  | 250ND non-return valve flanged on both ends. | No | 2
10.6 |  | Waste Activated Sludge (WAS) Pumps
Self priming pumps, complete with pump protections, manifolds valves and fittings and pipework supports for Waste Activated Sludge Pumping complete with motors, base plate and couplings
10.6.1 | MWP 15.1 | Manufacture, Supply and delivery | No | 1
10.6.2 | MWP 15.2 | Installation, testing and commissioning | No | 1
10.7 | MST 7 and DS 13 | SECONDARY SETTLING TANK
10.7.1 |  | Remove the existing two half bridges and their appurtenant equipment from the site, refurbish and recondition | Sum | 1
10.7.2 |  | Installation, testing and commissioning of two refurbished half bridges and appurtenant equipment (including new peripheral drive mechanism) | Sum | 1
CARRIED FORWARD
BROUGHT FORWARD
10.7.3 |  | Remove the existing centre pivot and turntable bearing and replace with new center pivot and turnable bearing | Sum | 1
10.7.4 |  | Refurbish, service and maintain the electric motor and issue maintenance certificate | Sum | 1
10.7.5 |  | Remove and replace the existing scum skimmer and sludge scrapers with new equipment | Sum | 1
10.7.6 |  | Remove and replace the flocculation baffles with new ones manufactured from 304 stainless steel | Sum | 1
10.7.7 |  | Remove and replace the existing scum baffles with new scum baffles (304 SS) | Sum | 1
10.7.8 |  | Remove the existing effluent weir and sludge buffle plates and replace with new 3CR12 plates | sum | 1
10.8 |  | Wash Water Pumps
Self priming pumps, complete with pump protections, manifolds valves and fittings and pipework supports for Wash water Pumping complete with motors, base plate and couplings and strainers on the suction side
10.8.1 | MWP 22.1 | Manufacture, Supply and delivery | No | 2
10.8.2 | MWP 22.2 | Installation, testing and commissioning | No | 2
10.8.3 |  | Refurbish, test and restore the existing washwater pumps and deliver to them to the Municipal Stores in Mogwase (and issue service certificates for the pumps) | No | 2
| MPW 15 DS 15 | Washwater Pumps - Valves
Extra-over Items 1.4 for supplying, laying and bedding of valves:
10.8.4 |  | 110ND handwheel cast iron (non-rising stem) resilient seal gate valve flanged on both ends. | No | 2
10.8.5 |  | 110ND handwheel cast iron (non-rising stem) resilient seal gate valve flanged on both ends. | No | 2
10.8.6 |  | 110ND non-return valve flanged on both ends. | No | 2
10.9 |  | DOCUMENTATION
10.9.1 | MGA 14.5 | Provision of Operation Manuals | Sum | 1
10.9.2 | MGA 14.5 | Provision of Maintenance Manuals | Sum | 1
10.9.3 |  | Develop new asset register for the plant (incoporating the old and new equipment on the plant | Sum | 1
10.9.4 | MGA 14.6 | Provision of Record Drawings | Sum | 1
10.9.5 | MGA 14.7 | Provision of Process Controllers Training Manuals | Sum | 1
10.9.6 | MGA 14.7 | Training of the Employers Operating staff | Sum | 1
10.1 |  | MISCELLANEOUS
10.10.1 |  | Supply and install 300 x 300 mm metal Mandatory, Warning and Safety signs around the inlet works, in accordance with SANS 1186 (Part 1 of 4) | Sum | 1
10.10.2 |  | Survival workplace First Aid Kit | No | 1
10.10.3 |  | Remove the existing handrails, sand down and regalvanise. Replace the corroded bolts, nuts and washers with new grade 4.8 hot dip galvanised bolts, nuts and washers | tons | 0.6
10.10.4 |  | Remove the Exisitng gearboxes, aerators, base plates refurbished and recondition, issue service certificates and deliver to municipal stores at Mogwase | No | 4
10.10.5 |  | Cut anchors flush with concrete and seal with zinc rich epoxy | No | 32
CARRIED FORWARD
BROUGHT FORWARD
10.10.6 |  | Remove the existing Waste Activated Sludge(WAS) valve, and replace with an extended spindle valve anchored to the wall, flanged spool make up piece and install a coupling for maintenance | Sum | 1
10.10.7 | DS15 | Supply and delivery of the groundwater relief valves for the anaerobic and anoxic tanks | No | 18
10.10.8 | DS15 | Installation, testing and commissioning the groundwater relief valves for anaerobic and anoxic tanks | No | 18
10.10.9 | DS 17 | Refurbish all the existing mild steel handstop at the inlet of the sludge Ponds | No | 4
10.10.10 | DS 17 | clean all the pipelines between the BNR, SSTs and the Sludge dams. Pipeline to be sand blasted and lined | sum | 1
TOTAL CARRIED FORWARD TO SUMMARY

## Electrical Works
MOSES KOTANE LOCAL MUNICIPALITY | [5 empty] | 1200C
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS | [5 empty] | SECTION 11: ELECTRICAL
Item Ref No. | Payment Refers SANS | Description | Unit | Quantity | Rate | Amount
R
11.1 |  | SECTION 11: ELECTRICAL
PRELIMINARIES AND GENERALS - ELECTRICAL
11.1.1 |  | Fixed portion | Sum | 1
11.1.2 |  | Time related portion | Sum | 1
11.1.3 |  | Co-operation and liason with Civil Contractor | Sum | 1
11.1.4 |  | Supervision | Month | 5
11.1.5 |  | Allow for an infrared (IR) photographic scanning of all the MCC including submission of a complete report to the electrical engineer by an independent specialist | Sum | 1
11.1.6 |  | Testing and commissioning of the electrical installation. | Sum | 1
11.1.7 |  | Issue certificate of compliance on the entire electrical installation including the standby generator. | Sum | 1
11.1.8 |  | Inspection and handing over | Sum | 1
11.1.9 |  | Mark up As Built drawings and submit them to the engineer for As Built purposes | Sum | 1
11.1.10 |  | Provision of Operating and Maintenance manuals to the enigneer | Sum | 1
11.1.11 |  | Provide for a master installation electrician for overseeing the electrical installation within the hazardous locations | Sum | 1
11.1.12 |  | Earthing and bonding complete electrical installation as required by SANS 10142-1 as amended, including other metal installations or steel structures. | Sum | 1
11.2 |  | MV BULK SERVICES
Supply, delivery and installation of 3 core XLPE insulated PVC bedded, steel wire amoured, PVC sheathed 6.35/11kV copper cables to SANS 1339 Type A drawn into cable sleeves, installed on cable trays /ladders or laid in open trenches and ducts.
120mm² x 3 core
11.2.8 |  | Supply | m | 5
11.2.9 |  | Install | m | 5
95mm² x 3 core
11.2.10 |  | Supply | m | 60
11.2.11 |  | Install | m | 60
70mm² x 3 core
11.2.12 |  | Supply | m | 10
11.2.13 |  | Install | m | 10
Cable Terminations and Joints
Supply and installation of MV cable terminations and joints complete with all accessories. 95mm² x 3 core
MV cable termination kit
11.2.14 |  | Supply | no | 2
11.2.15 |  | Install | no | 2
MV cable joint kit
11.2.16 |  | Supply | no | 1
11.2.17 |  | Install | no | 1
Main Earth Conductors
Supply, deliver and install all stranded earth copper conductors (both bare and PVC insulated) and lugs and the installation thereof, together with cables on trays, against structures, in sleeves and in wiring channels, including for the fixing and connecting thereof
70mm² bare copper
11.2.18 |  | Supply | m | 60
11.2.19 |  | Install | m | 60
CARRIED FORWARD
BROUGHT FORWARD
50mm² bare copper
11.2.20 |  | Supply | m | 5
11.2.21 |  | Install | m | 5
35mm² bare copper
11.2.22 |  | Supply | m | 10
11.2.23 |  | Install | m | 10
Main Earth Conductors Terminations
70mm² bare copper
11.2.24 |  | Supply | no | 6
11.2.25 |  | Install | no | 6
50mm² bare copper
11.2.25 |  | Supply | no | 4
11.2.26 |  | Install | no | 4
35mm² bare copper
11.2.27 |  | Supply | no | 2
11.2.28 |  | Install | no | 2
Miniature Substation (Minisub)
Supply ,delivery and installation of 800kVA 11000/420V, Type B miniature substation, minisub (as specified)
11.2.29 |  | Supply | no | 1
11.2.30 |  | Install | no | 1
Concrete plinth suitable for a 800kVA Type B minisub.
11.2.31 |  | Supply | no | 1
11.2.32 |  | Install | no | 1
Miscellaneous
11.2.33 |  | Switching and phasing MV cable | sum | 1
11.2.34 |  | Pressure testing of MV cable | sum | 1
MV Trenching
Excavation 1000mm deep and 400mm wide trench including backfilling and compacting
11.2.35 |  | In earth | m3 | 25
11.2.36 |  | Soft rock extra over earth | m3 | 18
11.2.37 |  | Hard rock | m3 | 13
Imported soft sand bedding of 150mm under the cable and above cable (when required by coil conditions)
11.2.38 |  | Supply | m3 | 15
11.2.39 |  | Install | m3 | 15
MV cable marker tape laid in an open trench 150mm above the cable along the length of the cable
11.2.40 |  | Supply | m | 60
11.2.41 |  | Install | m | 60
1000mm L X 300m W X 60mm H Concrete slabs or blocks laid in an open trench 150mm above the cable marker tape along the length of the cable
11.2.42 |  | Supply | no | 30
11.2.43 |  | Install | no | 30
5mm nylon drawn cable drawn into spare sleeves
11.2.44 |  | Supply | m | 50
11.2.45 |  | Install | m | 50
250mm High trancated pyramid cable route marker with stainless steel insert engraved with the cable dedails eg, "MV 70mm²X3C CABLE". installed to protrude 150mm above ground and every 35m along and at the cable route direction change.
11.2.46 |  | Supply | no | 4
11.2.47 |  | Install | no | 4
Double skin brick manhole, 1000mm x 1000mm x 1000mm deep minimum inside dimensions with heavy duty cover
11.2.48 |  | Supply | no | 1
11.2.49 |  | Install | no | 1
CARRIED FORWARD
BROUGHT FORWARD
Kabelflex, High density polyethylene (HDPE) with corrugated double wall construction cable sleeves laid in open trenches, ducts, cast into slabs etc. including all couplings, joints, bends and other accessories.
NOTE: Spare sleeves for future use to be sealed at both ends
160mm diameter
11.2.50 |  | Supply | m | 40
11.2.51 |  | Install | m | 40
110mm diameter
11.2.52 |  | Supply | m | 25
11.2.53 |  | Install | m | 25
50mm diameter
11.2.54 |  | Supply | m | 5
11.2.55 |  | Install | m | 5
90 degrees slow bend for 160mm dia. Sleeve
11.2.56 |  | Supply | No. | 2
11.2.57 |  | Install | No. | 2
90 degrees slow bends for 110mm dia. sleeve
11.2.58 |  | Supply | No. | 2
11.2.59 |  | Install | No. | 2
1.6mm galvanised draw wire drawn into
conduit or sleeve
11.2.60 |  | Supply | m | 85
11.2.61 |  | Install | m | 85
Label cables on both ends with numbering beads or non-corroding straps to indicate their connection points.
11.1.62 |  | Supply | sum | 1
11.1.63 |  | Install | sum | 1
Earthing
Earthing of all MV equipment as required by regulations as specified. Earth mat resistance to be less than one ohm.
11.1.64 |  | Provisional sum to carry out the above work | sum | 1
11.1.65 |  | Profit and attendance on item 2.10.1 | % | 5
11.3 |  | LOW VOLTAGE DISTRIBUTION
CABLES
Supply, deliver and install the specified Low Voltage Cable as per LV feeds required from the transformer, substation and DB's:
From minisub to MCC 1: 4 off 185mm² x 4-core ECC PVC SWA PVC in parallel
11.2.1 |  | Supply | m | 130
11.2.2 |  | Install | m | 130
From MCC 1 to existing generator set: 2 off 70mm² x 4-core ECC PVC SWA PVC in parallel
11.2.3 |  | Supply | m | 36
11.2.4 |  | Install | m | 36
From MCC 1 to MCC 2: 70mm² x 4-core ECC PVC SWA PVC
11.2.5 |  | Supply | m | 235
11.2.6 |  | Install | m | 235
From MCC 1 to MCC 3: 16mm² x 4-core ECC PVC SWA PVC
11.2.7 |  | Supply | m | 125
11.2.8 |  | Install | m | 125
From MCC 1 to the mixers (Anaerobic & Anoxic tanks): 6mm² x 4-core ECC PVC SWA PVC
11.2.13 |  | Supply | m | 610
11.2.14 |  | Install | m | 610
From MCC 1 to aerators 1 to 4: 35mm² x 4-core PVC SWA PVC
11.2.15 |  | Supply | m | 282
11.2.16 |  | Install | m | 282
CARRIED FORWARD
BROUGHT FORWARD
From MCC 1 to the RAS and WAS pumps: 4mm² x 4-core PVC SWA PVC
11.2.17 |  | Supply | m | 185
11.2.18 |  | Install | m | 185
From MCC 1 to the clarifier tanks: 4mm² x 3-core PVC SWA PVC
11.2.19 |  | Supply | m | 105
11.2.20 |  | Install | m | 105
From MCC 2 to head of works pumps: 4mm² x 4-core PVC SWA PVC
11.2.23 |  | Supply | m | 200
11.2.24 |  | Install | m | 200
From MCC 3 to centrifugal pumps: 4mm² x 4-core PVC SWA PVC
11.2.29 |  | Supply | m | 60
11.2.30 |  | Install | m | 60
From MCC 3 to Chlorine Building DB: 16mm² x 3-core PVC SWA PVC
11.2.31 |  | Supply | m | 60
11.2.32 |  | Install | m | 60
From MCC 2 to Head of Works DB: 16mm² x 3-core PVC SWA PVC
11.2.33 |  | Supply | m | 20
11.2.34 |  | Install | m | 20
From MCC 1 to MCC 1 DB: 16mm² x 3-core PVC SWA PVC
11.2.35 |  | Supply | m | 10
11.2.36 |  | Install | m | 10
Termination of 600/1000V PVC grade copper
cable connection MCCB's with crimped lugs
185mm² x 4-core ECC PVC SWA PVC
11.2.45 |  | Supply | no | 8
11.2.46 |  | Install | no | 8
70mm² x 4-core ECC PVC SWA PVC
11.2.47 |  | Supply | no | 6
11.2.48 |  | Install | no | 6
35mm² x 4-core ECC PVC SWA PVC
11.2.49 |  | Supply | no | 2
11.2.50 |  | Install | no | 2
25mm² x 4-core ECC PVC SWA PVC
11.2.51 |  | Supply | no | 6
11.2.52 |  | Install | no | 6
16mm² x 4-core ECC PVC SWA PVC
11.2.53 |  | Supply | no | 4
11.2.54 |  | Install | no | 4
10mm² x 4-core ECC PVC SWA PVC
11.2.55 |  | Supply | no | 8
11.2.56 |  | Install | no | 8
16mm² x 3-core PVC SWA PVC
11.2.57 |  | Supply | no | 2
11.2.58 |  | Install | no | 2
10mm² x 3-core PVC SWA PVC
11.2.59 |  | Supply | no | 20
11.2.60 |  | Install | no | 20
6mm² x 4-core PVC SWA PVC
11.2.61 |  | Supply | no | 18
11.2.62 |  | Install | no | 18
6mm² x 3-core PVC SWA PVC
11.2.63 |  | Supply | no | 74
11.2.64 |  | Install | no | 74
4mm² x 4-core PVC SWA PVC
11.2.65 |  | Supply | no | 52
11.2.66 |  | Install | no | 52
CARRIED FORWARD
BROUGHT FORWARD
4mm² x 3-core PVC SWA PVC
11.2.67 |  | Supply | no | 8
11.2.68 |  | Install | no | 8
MAIN EARTH CONDUCTORS
Supply, deliver and install all stranded earth copper conductors (both bare and PVC insulated) and lugs and the installation thereof, together with cables on trays, against structures, in sleeves and in wiring channels, including for the fixing and connecting thereof
70mm² bare copper
11.2.69 |  | Supply | m | 10
11.2.70 |  | Install | m | 10
25mm² bare copper
11.2.71 |  | Supply | m | 10
11.2.72 |  | Install | m | 10
MAIN EARTH CONDUCTORS TERMINATIONS
70mm² bare copper
11.2.73 |  | Supply | no | 4
11.2.74 |  | Install | no | 4
25mm² bare copper
11.2.75 |  | Supply | no | 4
11.2.76 |  | Install | no | 4
SLEEVES, CABLE BASKETS AND DUCTING
The supply and installation of all cable trays installed in ceiling voids complete with support structure, bends, joints, reducing sections, cross pieces, angle pieces and expanding joints, threaded rod braces, channels and straps and accessories
sleeves for future use to be sealed at both ends
110mm sleeve
11.2.77 |  | Supply | m | 120
11.2.78 |  | Install | m | 120
50mm sleeve
11.2.79 |  | Supply | m | 25
11.2.80 |  | Install | m | 25
90 degrees slow bend for 110mm dia. Sleeve
11.2.81 |  | Supply | no | 14
11.2.82 |  | Install | no | 14
90 degrees slow bends for 50mm dia. sleeve
11.2.83 |  | Supply | no | 8
11.2.84 |  | Install | no | 8
1.6mm galvanised draw wire drawn into
conduit or sleeve
11.2.85 |  | Supply | m | 180
11.2.86 |  | Install | m | 180
CARRIED FORWARD
BROUGHT FORWARD
The Supply and installation of all heavy duty
cable trays installed in ceiling voids complete with support structure, bends, joints, reducing sections, cross pieces, angle pieces and expanding joints, threaded rod braces, channels and straps and accessories. Cable ladder to be galvanised and powder coated orange.
Heavy duty 450mm wide cable ladder
11.2.99 |  | Supply | m | 75
11.2.100 |  | Install | m | 75
Heavy duty 600mm wide cable tray
11.2.101 |  | Supply | m | 75
11.2.102 |  | Install | m | 75
Heavy duty 400mm wide welded wiremesh basket.
11.2.103 |  | Supply | m | 150
11.2.104 |  | Install | m | 150
MCC PANELS, MAIN DISTRIBUTION BOARDS AND DISTRIBUTION BOARS.
Supply and install distribution boards as specified and drawn on schematic diagrams and in positions as indicated on relevant drawngs
Main MCC or MCC 1
11.2.105 |  | Supply | no | 1
11.2.106 |  | Install | no | 1
MCC 2 - HW
11.2.107 |  | Supply | no | 1
11.2.108 |  | Install | no | 1
MCC 3 - CHL
11.2.109 |  | Supply | no | 1
11.2.110 |  | Install | no | 1
MCC 1 Building Local DB
11.2.113 |  | Supply | no | 1
11.2.114 |  | Install | no | 1
MCC 2 Building Local DB
11.2.115 |  | Supply | no | 1
11.2.116 |  | Install | no | 1
MCC 3 Building Local DB
11.2.117 |  | Supply | no | 1
11.2.118 |  | Install | no | 1
Supply and install the following switchgear on distribution boards as and when required. Switchgear shall match the existing switchgear in order to maintain the same switchgear make in all DB's.
10A, 240V, 6kA circuit breaker
11.2.121 |  | Supply | no | 6
11.2.122 |  | Install | no | 6
CARRIED FORWARD
BROUGHT FORWARD
20A, 240V, 6kA circuit breaker
11.2.123 |  | Supply | no | 2
11.2.124 |  | Install | no | 2
20A, 420V, 6kA circuit breaker
11.2.125 |  | Supply | no | 2
11.2.126 |  | Install | no | 2
50A, 420V, 6kA circuit breaker
11.2.127 |  | Supply | no | 2
11.2.128 |  | Install | no | 2
70A, 420V, 6kA circuit breaker
11.2.129 |  | Supply | no | 2
11.2.130 |  | Install | no | 2
LV Trenching
Excavation 600mm deep and 400mm wide trench including backfilling and compacting
11.2.131 |  | In earth | m3 | 167
11.2.132 |  | Soft rock extra over earth | m3 | 49
11.2.133 |  | Hard rock | m3 | 25
Imported soft sand bedding of 150mm under the cable and above cable (when required by soil conditions)
11.2.134 |  | Supply | m3 | 7
11.2.135 |  | Install | m3 | 7
MV cable marker tape laid in an open trench 150mm above the cable along the length of the cable
11.2.136 |  | Supply | m | 105
11.2.137 |  | Install | m | 105
250mm High trancated pyramid cable route marker with stainless steel insert engraved with the cable dedails eg, "LV 16mm²X4C CABLE". installed to protrude 150mm above ground and every 35m along and at the cable route direction change.
11.2.138 |  | Supply | no | 7
11.2.139 |  | Install | no | 7
Earthing
Earthing of all LV equipment or installation as required including LV room earth mat, as specified. Earth mat resistance to be less than one ohm.
Povision of earthing as per regulations.
11.2.140 |  | Provisional sum to carry out the work above | sum | 1
11.2.141 |  | Profit and attendance on item 2.11.1 | % | 5
Lightning Protection System
Design, supply and install lightning protection system (LPS) as described in the specification. The design, supply and installation of the LPS shall be done by the LPS specialist. LPS design and installation shall comply with applicable standards as amended.
11.2.142 |  | Provisional sum to carry out the work above | sum | 1
11.2.143 |  | Profit and attendance on item 2.12.1 | % | 5
CARRIED FORWARD
BROUGHT FORWARD
11.3 |  | GENERAL POWER RETICULATION
CONDUITS
PVC CONDUIT supplied and installed, including couplings, cutting, bending, fixing etc. as per specification in concrete, brickwork and on surface in voids.
20mm diameter conduit
11.3.1 |  | Supply | m | 100
11.3.2 |  | Install | m | 100
GALVANISED STEEL CONDUIT supplied and installed, including outlet Box, cover plate, couplings, cutting, bending, fixing etc. as per specification in concrete (floor slab), brickwork and on surface in voids.
20mm diameter conduit
11.3.3 |  | Supply | m | 3000
11.3.4 |  | Install | m | 300
CONDUIT OUTLET BOXES
Galvanised 100 x 100x 50mm conduit outlet box and cover plate to suit any number, size or type of entries, fixed in roofs or in and including recess in brickwork or cast in concrete
11.3.5 |  | Supply | no | 100
11.3.6 |  | Install | no | 100
Galvanised 100 x 50x 50mm conduit outlet box and cover plate to suit any number, size or type of entries, fixed in roofs or in and including recess in brickwork or cast in concrete
11.3.7 |  | Supply | no | 10
11.3.8 |  | Install | no | 10
Round galvanised conduit box (60 - 65mm) diameter
11.3.9 |  | Supply | no | 100
11.3.10 |  | Install | no | 100
CONDUCTORS
PVC insulated 600/1000 V stranded copper conductors, drawn into conduit, wire ways and/or sleeves :
4 mm² conductor
11.3.11 |  | Supply | m | 600
11.3.12 |  | Install | m | 600
2.5 mm²
11.3.13 |  | Supply | m | 600
11.3.14 |  | Install | m | 600
Bare stranded copper earth conductors, drawn into conduit,
2.5 mm²
11.3.15 |  | Supply | m | 300
11.3.16 |  | Install | m | 300
CARRIED FORWARD
BROUGHT FORWARD
SWITCHES, SOCKET OUTLETS AND ACCESSORIES, ETC.
Switched socket outlet complete with cover plate fixed in flush box or flush in lid of power skirting or in box on wall.
16A 3-pin normal single flush mounted switched socket outlet with 2-pin outlet
11.3.17 |  | Supply | no | 16
11.3.18 |  | Install | no | 16
16A 3-pin normal double flush mounted switched socket outlet
11.3.19 |  | Supply | no | 3
11.3.20 |  | Install | no | 3
16A 3-pin normal single surface mounted switched socket outlet
11.3.21 |  | Supply | no | 3
11.3.22 |  | Install | no | 3
16A 3-pin normal double surface mounted switched.
11.3.23 |  | Supply | no | 2
11.3.24 |  | Install | no | 2
100x100x50mm Cover plates where necessary
11.3.27 |  | Supply | no | 10
11.3.28 |  | Install | no | 10
100x50x50mm Cover plates where necessary
11.3.29 |  | Supply | no | 8
11.3.30 |  | Install | no | 8
20A double pole surface mounted isolator
11.3.31 |  | Supply | no | 3
11.3.32 |  | Install | no | 3
30A double pole surface mounted isolator
4.4.17 |  | Supply | no | 2
4.4.18 |  | Install | no | 2
20A triple pole surface mounted isolator
11.3.33 |  | Supply | no | 3
11.3.34 |  | Install | no | 3
30A triple pole surface mounted isolator
11.3.35 |  | Supply | no | 2
11.3.36 |  | Install | no | 2
60A triple pole surface mounted isolator
11.3.37 |  | Supply | no | 2
11.3.38 |  | Install | no | 2
Outdoor 100A triple pole surface mounted isolator
11.3.41 |  | Supply | no | 1
11.3.42 |  | Install | no | 1
CARRIED FORWARD
BROUGHT FORWARD
Labelling of all power points, socket outlets with circuit numbers, number of socket outlet in the circuit and DB supplying that circuit.
11.3.43 |  | Supply | sum | 1
11.3.44 |  | Install | sum | 1
300X300X65mm access floor box suitable to accommodate 6 off modular outlets supplied complete with 3 off power point outlets and 2 off data point and 1 off HDMI point.
11.3.45 |  | Supply | No | 1
11.3.46 |  | Install | No | 1
11.4 |  | GENERAL LIGHTING RETICULATION
CONDUITS
Galvanised conduit supplied and installed, including couplings, cutting, bending, fixing etc. as per specification in concrete, brickwork and on surface in voids.
20 mm
11.4.1 |  | Supply | m | 200
11.4.2 |  | Install | m | 200
25 mm
11.4.3 |  | Supply | m | 15
11.4.4 |  | Install | m | 15
CONDUIT OUTLET BOXES
Galvanised 100 x 50 x 50mm conduit outlet box and cover plate to suit any number, size or type of entries, fixed in roofs or in and including recess in brickwork or cast in concrete
11.4.5 |  | Supply | no | 10
11.4.6 |  | Install | no | 10
Galvanised (60-65)mm diameter shallow type conduit outlet box and cover plate to suit any number, size or type of entries, fixed in roofs or in and including recess in brickwork or cast in concrete
11.4.7 |  | Supply | no | 50
11.4.8 |  | Install | no | 50
CONDUCTORS
2.5 mm² Conductor
11.4.11 |  | Supply | m | 1500
11.4.12 |  | Install | m | 1500
2.5 mm² BCEW
11.4.15 |  | Supply | m | 750
11.4.16 |  | Install | m | 750
SURFIX CABLE (BLACK)
Supply and Install
2.5mm² X 4-core + earth wire
11.4.17 |  | Supply | m | 100
11.4.18 |  | Install | m | 100
SWITCHES AND ACCESSORIES, ETC.
16A One lever one way flush mounted light switch
11.4.19 |  | Supply | no | 5
11.4.20 |  | Install | no | 5
16A One lever one way surface mounted light switch
11.4.23 |  | Supply | no | 1
11.4.24 |  | Install | no | 1
16A One lever two way flush mounted light switch
11.4.25 |  | Supply | no | 2
11.4.26 |  | Install | no | 2
20A Photo-electric daylight sensitive switch
11.4.29 |  | Supply | no | 6
11.4.30 |  | Install | no | 6
CARRIED FORWARD
BROUGHT FORWARD
SOCKET OUTLET FOR LIGHT FITTINGS
FITTINGS
LIGHT FITTINGS SUPPLY & INSTALL
Type C1: 18W weatherproof, IP65 LED bulkhead light fitting as specified. Light fitting to have a black trim.
11.4.33 |  | Supply | no | 11
11.4.34 |  | Install | no | 11
Type L1: 100W LED floodlight light fitting
11.4.35 |  | Supply | no | 25
11.4.36 |  | Install | no | 25
Type F1: 35W LED corrosion resisitant streetlight light fitting as specified.
11.4.37 |  | Supply | no | 24
11.4.38 |  | Install | no | 24
Type G1: 32W surface mounted vapour-proof light fitting as specified.
11.4.39 |  | Supply | no | 10
11.4.40 |  | Install | no | 10
Type C1E: 18W weatherproof, IP65 LED bulkhead light fitting complete with battery pack, as specified
11.4.41 |  | Supply | no | 5
11.4.42 |  | Install | no | 5
Type G1E: 32W surface mounted vapour-proof light fitting complete with battery pack, as specified.
11.4.43 |  | Supply | no | 7
11.4.44 |  | Install | no | 7
Type D: Surface mounted single sided exit signage with 'Exit' sign as specified
11.4.47 |  | Supply | no | 2
11.4.48 |  | Install | no | 2
10.5M HDG plant step pole supplied complete with 4 way streetlight spigot
11.4.51 |  | Supply | no | 5
11.4.52 |  | Install | no | 5
Type C2: 18W weatherproof, IP65 LED bulkhead light fitting as specified. Light fitting to have a white trim.
11.4.53 |  | Supply | no | 12
11.4.54 |  | Install | no | 12
Type A1: 30W 600X600mm recessed LED panel light fitting as specified.
11.4.55 |  | Supply | no | 35
11.4.56 |  | Install | no | 35
Type A1E: Same as Type A1, but equipped with emergency battery pack.
11.4.57 |  | Supply | no | 7
11.4.58 |  | Install | no | 7
Type B1: 18W recessed LED downlight light fitting as specified.
11.4.59 |  | Supply | no | 17
11.4.60 |  | Install | no | 17
Type B1E: Same as Type B1E, but equipped with emergency battery pack.
11.4.61 |  | Supply | no | 4
11.4.62 |  | Install | no | 4
Type B2: Slim decorative surface mounted 18W LED down light, as specified.
11.4.63 |  | Supply | no | 36
11.4.64 |  | Install | no | 36
CARRIED FORWARD
BROUGHT FORWARD
11.5 |  | ELECTRONIC SYSTEMS
Supply and install the required elements as specified below to accommodate Data and Telephone support infrastructure of conduit, outlet boxes and blank cover plates.
Flush mounted telephone DB with dimensions of 450 x 300 x 250mm deep with door fitted with door latch.
11.5.1 |  | Supply | no | 1
11.5.2 |  | Install | no | 1
Galvanised conduit in ceiling voids, in wall chases and on surface:
25mm Conduit:
11.5.3 |  | Supply | m | 600
11.5.4 |  | Install | m | 600
Galvanised flush mounted draw boxes with white enamel finished cover plates fitted with chromium plated screws.
100 x 100x 50 mm draw boxes
11.5.5 |  | Supply | no | 110
11.5.6 |  | Install | no | 110
100 x 100x 50 mm cover plates
11.5.7 |  | Supply | no | 15
11.5.8 |  | Install | no | 15
(60-65)mm diameter round draw box:
11.5.9 |  | Supply | no | 30
11.5.10 |  | Install | no | 30
(60-65)mm diameter round cover plate to fit round draw box
11.5.11 |  | Supply | no | 40
11.5.12 |  | Install | no | 40
TELEPHONE AND DATA INSTALLATION
Data outlet for surface mounting with 100 x 50 x 50mm coverplate
11.5.13 |  | Supply | no | 5
11.5.14 |  | Install | no | 5
Data outlet for mounting in powerskirting
11.5.15 |  | Supply | no | 5
11.5.16 |  | Install | no | 5
MEDIUM DUTY WELDED MESH CABLE TRAY
The supply and installation of welded mesh cable trays installed in ceiling voids complete with support structure, bends, joints, reducing sections, cross pieces, angle pieces and expanding joints, threaded rod braces, channels and straps and accessories
200mm Wide welded mesh cable tray
11.5.17 |  | Supply | m | 80
11.5.18 |  | Install | m | 80
200mm Wide welded mesh cable tray: Bends
11.5.19 |  | Supply | no | 12
11.5.20 |  | Install | no | 12
200mm Wide welded mesh cable tray: Tee's
11.5.21 |  | Supply | no | 6
11.5.22 |  | Install | no | 6
PVC COMPACT MINI TRUNKING
Supply and install PVC compact mini trunking complete with lid and all its standard accessories as may be required when installing it
40mm x 16mm, YT3 mini trunking
11.5.23 |  | Supply | m | 30
11.5.24 |  | Install | m | 30
25mm x 16mm, YT2 mini trunking
11.5.25 |  | Supply | m | 15
11.5.26 |  | Install | m | 15
CARRIED FORWARD
BROUGHT FORWARD
EARTHING
300mm L x 200mm W x 3mm H earth bar with 8mm bolts and nuts for 16mm2 insulated copper conductor from the server room to the substation earth.
11.5.27 |  | Supply | no | 1
11.5.28 |  | Install | no | 1
TELECOMMUNICATIONS MANHOLES
Double skin brick manhole, 800mm x 800mm x 800mm deep minimum inside dimensions with heavy duty cover
11.5.29 |  | Supply | no | 14
11.5.30 |  | Install | no | 14
11.6 |  | STANDBY GENERATOR
Manufacture, supply, off loading, installation and commissioning of a 60kVA prime, three phase outdoor standby generator including control panel as described in the specification. Price to include a control system effecting automatic mains failure starting without synchronisation with mains.
Include the following in the generator price: Battery Battery charger Water jacket heater Main outgoing circuit breaker Motorised change-over isolator set Sound attenuation weatherproof canopy. Rigging GSM enabled controller Generator base tank to contain diesel fuel sufficient to provide a backup time of 8 hours minimum at full load.
SECTION 7: STANDBY GENERATOR SET
Existing Standby Generator
11.6.16 |  | Refurbish where necessary and maintain the existing standby generator. | sum | 1
11.6.17 |  | Provide a 12 month maintenance to the existing generator | sum | 1
11.6.18 |  | Issue standby generator maintenance logbook | sum | 1
CARRIED FORWARD
BROUGHT FORWARD
SECTION 8: PROVISIONAL SUMS
11.7 |  | Provisional Sums For Various System and Installations
Power Factor Correction
11.7.1 |  | Provision for the supply and installation of a 200kVAr power factor correction (PFC) unit. The PFC unit to be correctly sized as required prior to specifying and procuring. | sum | 1 | 300000 | 300000
11.7.2 |  | Allow for profit on above | % | 300000
TOTAL CARRIED FORWARD TO SUMMARY

## Summary Page Original
MOSES KOTANE LOCAL MUNICIPALITY
TENDER NUMBER: 005/MKLM/2024/2025
REFURBISHMENT OF MOGWASE WASTEWATER TREATMENT WORKS |  | SUMMARY
SECTION | DESCRIPTION ENGINEER'S COST ESTIMATE | AMOUNT (R)
1 | PRELIMINARY AND GENERAL
2 | DAYWORKS
3 | INLET WORKS AND INLET BUILDINGS
4 | BIOLOGICAL REACTOR
5 | SECONDARY SETTLING TANK
6 | RETURN ACTIVATED PUMPS
7 | SLUDGE PONDS
8 | CHLORINE BUILDING
9 | WASH WATER PUMPS
10 | MECHANICAL
11 | ELECTRICAL WORKS
TOTAL CONSTRUCTION COST
ADD CONTINGENCIES (10%)
SUB TOTAL
ESCALATION AT 5%
SUB TOTAL
ALLOWANCE FOR VAT 15.0%
TOTAL TENDER SUM